	
	



	[image: image1.wmf]
	Customer: Mustang/Sandridge/IAG
Sales Order No.: 294100
Project: M555BA Compressor Drivelines



CASING VIBRATION READINGS - BASELINE DATA

NOTE:
YORK RECOMMENDS BASE–LINE VIBRATION READINGS BE TAKEN AFTER START-UP.  ONLY THIS WAY CAN LATER INTERPRETATIONS OF VIBRATION READINGS BE MEANINGFUL.

BEFORE PERFORMING VIBRATION ANALYSIS CHECK THE FOLLOWING:

1. Is the package mounted on a rigid concrete foundation?  Refer to the Instructions to Erecting Engineer drawing 560D0124 (centrifugal compressors) or as specified in the Frick Manual S70-270 IB/FEB93 (screw compressors).  Improper mounting will increase the vibration levels throughout the package.

2. Are the pipes connecting the package to the system supported correctly?  (Pipes not supported properly will increase 2xRPM vibration levels)

3. Is the coupling installed properly between the motor and the compressor?  (Reference the IOM)

4. Check the cold alignment. For a screw compressor, it should not exceed .004.  For a centrifugal compressor, it should match the cold misalignment requirements shown in the IOM.  Run the compressor until operating temperature is reached, then check the hot alignment.  (Alignment procedure is covered in the IOM)

5. For screw compressors, the Volumizer or Slide Stop calibration needs to be checked.  (The Volumizer potentiometer calibration is covered in the IOM).  For centrifugal compressors, the capacity control must be tuned to minimize cyclic loading and unloading.

6. Load the compressor to design conditions.  If this is not possible, make sure that readings are taken at the same compressor loading.

7. First, take vibration readings on the motor at both the inboard and outboard bearings.  (Take vibration readings at each location in Inches per second peak, vs. a scale of 1000 Hz, then take a second set of readings in G’s acceleration peak, vs. a scale of 10,000 Hz) 


Note:
For antifriction bearings (screw compressor and most NEMA motor frames), acceleration readings (G's) are of primary interest.  On sleeve bearings (centrifugal compressors, large motors and gears), velocity readings in inches per second are of primary interest.

8. Second, take vibration readings on the compressor at each bearing location.  On screw compressors, monitor both the male and female rotor on the inboard and outboard bearings.  On screw compressors take three readings at each bearing location in the vertical, horizontal and axial directions.  On each axis, take readings in both vibration (IPS), and acceleration (G’s) spike energy.  On centrifugals, measure velocity (IPS) in each of three axes on the housings as close as possible to the bearings (on the sump end, measure at the sump flange to split case junction).

9. Take vibration readings on the gearbox on centrifugal systems.  Sketch the box and show the reading locations and types.

On screw compressor packages, it is common to see vibration readings on our packages at frequencies higher than input speed.  This results from gas pulsation at the mesh frequency of the rotors.  Mesh frequency depends on gear ratio (RXB/RXF) and number or male lobes.  Refer to the VIBRATION SEVERITY GUIDELINES in Section 7 of this manual.

Compare readings to the setpoints shown in Section 12 when applicable.

 FORMCHECKBOX 
 RWB   FORMCHECKBOX 
 RWF   FORMCHECKBOX 
 OTHER
SCREW COMPRESSOR VIBRATION 

	Job Name:
	     
	Frick Order #
	     

	Compressor Serial  #
	     
	Equipment:
	     

	Type Driver & HP:
	     
	Running Hours:
	     

	Vibration Analyzer:
	     
	Type Coupling:
	     

	Type Refrigerant:
	     
	Testing Date:
	     

	National Board #:
	     
	Technician:
	     

	Vibration Readings:
	 FORMCHECKBOX 
  IPS   FORMCHECKBOX 
G's


OPERATING CONDITIONS
	SUCTION
	DISCHARGE
	OIL
	SEPARATOR
	Slide Valve Position             %

	PSIg      
	PSIg      
	PSIg      
	temp.      
	V.I. Ratio      

	temp.       
	temp.      
	temp.      
	
	FLA                                       %


Male Outboard
Male Inboard
Motor Inboard
	Horizontal
	      
	 Overall
	
	Horizontal
	     
	 Overall
	
	Horizontal
	     
	 Overall

	Vertical
	     
	 Overall
	
	Vertical
	     
	 Overall
	
	Vertical
	     
	 Overall

	Axial
	     
	 Overall
	
	Axial
	     
	 Overall
	
	Axial
	     
	 Overall


[image: image2.wmf][image: image3.wmf]
Female Outboard
Female Inboard
Motor Outboard
	Horizontal
	      
	 Overall
	
	Horizontal
	     
	 Overall
	
	Horizontal
	     
	 Overall

	Vertical
	     
	 Overall
	
	Vertical
	     
	 Overall
	
	Vertical
	     
	 Overall

	Axial
	     
	 Overall
	
	Axial
	     
	 Overall
	
	Axial
	     
	 Overall


 FORMCHECKBOX 
 RXF  FORMCHECKBOX 
 RXB  FORMCHECKBOX 
 OTHER
SCREW COMPRESSOR VIBRATION 

	Job Name:
	        
	Frick Order #
	     

	Compressor Serial  #
	     
	Equipment:
	     

	Type Driver & HP:
	     
	Running Hours:
	     

	Vibration Analyzer:
	     
	Type Coupling:
	     

	Type Refrigerant:
	     
	Testing Date:
	     

	National Board #:
	     
	Technician:
	     

	Vibration Readings:
	 FORMCHECKBOX 
IPS    FORMCHECKBOX 
 G's
	
	


OPERATING CONDITIONS

	SUCTION
	DISCHARGE
	OIL
	SEPARATOR
	Slide Valve Position
	     
	%

	press
	      
	press
	     
	Press
	     
	temp.
	     
	V.I. Ratio
	     
	

	temp.
	      
	temp.
	     
	temp.
	     
	 
	 
	F.L.A.
	     
	%


	Compr Female Inboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Compr Female Outboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall

	Motor Outboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall


	Comp Male Outboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall


	Motor Outboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall


	Compr Male Inboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	 Compr Driveshaft Bearing

	Horizontal
	     
	Overall


 FORMCHECKBOX 
M-COMPR  FORMCHECKBOX 
 OTHER
CENTRIFUGAL COMPRESSOR VIBRATION 

	Job Name:
	Sandridge Energy 
	Frick Order #
	294100

	Compressor Serial  #
	     
	Equipment:
	     

	Type Driver & HP:
	Motor / 4000
	Running Hours:
	     

	Vibration Analyzer:
	     
	Gear Ratio:
	1.825:1

	Gas:
	R-134a
	Testing Date:
	     

	Compr Speed:
	3233
	Technician:
	     

	Vibration Readings:
	Velocity,  FORMCHECKBOX 
IPS 
	
	


OPERATING CONDITIONS

	SUCTION
	DISCHARGE
	COMPR OIL
	GEAR OIL
	PERCENT DESIGN LOAD
	      
	%

	Press
	      
	Press
	     
	Press
	     
	Press
	     
	PRV Position
	     
	%

	Temp
	     
	Temp
	     
	Temp
	     
	 Temp
	     
	F.L.A.
	     
	%


	Gear HS Ext End

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall

	Gear HS Blind End

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall


	Motor Outboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall


	Compr Outboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall



	Comp Inboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall

	Gear LS Blind End

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall

	Motor Outboard

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall

	Gear LS Ext End

	Horizontal
	     
	Overall

	Vertical
	     
	Overall

	Axial
	     
	Overall




















































































































































































































� EMBED Word.Picture.8  ���





MOTOR








_993476834.doc


�












